## Slide 2: REMUS RealTime Evolution : KAFKA 08.03.2019
HSE-CEN-CO Section
Alexandru Savulescu on behalf of REMUS TEAM

## Slide 3: Radiation Protection and Environment Monitoring at CERN (Context)
Environment Monitoring:
Many more!
Stray Radiation (x43)
Ventilation (x47)
Water (x14)
Gamma Radiation (x46)
Radiation Protection:
Many more!
Hand-Foot Contamination (x60)
LHC Tunnel
ATLAS
CMS
LHCb
ALICE
Radiation with Alarm Units (x100)
50 km Accelerator Tunnel - 60 Access Points - 160 Experiments - 8,000 Radiation Workers
~500 Monitoring Stations:
  24 different types
  Commercial Off-the-Shelf & Internally Developed Stations
  Surface and Underground areas
~3,200 Measurement Channels:
  1,000 measurements archived / second
  Workplace and Environment Safety
  Reporting to authorities:
  - Nature and quantities of emitted ionizing radiation
  - Conventional environmental measured values

## Slide 4: REMUS RealTime Visualization - DIP
Issues
Synchronous
No ACLs
Single Point of Failure
CCC & Other control rooms
Issues
DIP WinCC OA driver not 100% redundant compatible
High maintenance

## Slide 5: REMUS RealTime Visualization - KAFKA
CCC & Other control rooms
Added value
DIP is not a SPOF for RT
DIP Buffer Server is gone
Asynchronous data streams
ATLAS, CMS, TI, ???

## Slide 6: WinCC OA KAFKA Streaming
In-house WinCC OA Kafka driver
  WinCC OA driver API
  librdkafka + cppkafka
One REMUS KAFKA publisher
  Actually two 
    REMUS is a redundant system, only one publisher is active at a time
REMUS data streams
  Unique measurement as JSON
    REMUS JSON format
      {"id":<STREAM ID>,"value":<VAL>, "timestamp":<TS>, "unit":<UNIT>, "flags":{<FLAGS>}}
    KAFKA key: <STREAM ID>
  Built from one or more source DPEs
  Other streams in the near future (parametrizations, events, etc.)
  Can be any string or data format

## Slide 7: KAFKA Streaming – WinCC OA: REMUS Implementation
Dedicated DPs for streaming
  Isolated from the device model DPs
Generically addressed with the WinCC OA Kafka driver
    KAFKA TOPIC$KAFKA KEY$DEBOUNCINGTIME
    Ex: remustest$11134$0
Debouncing mechanism
  Allows data streams built from unsynchronized DPEs to stream exactly once
  Implemented in the WinCC OA Kafka driver
    Debouncing time period sent to the driver for each stream
    DEBOUNCINGTIME = 0 direct streaming with no debouncing

## Slide 8: KAFKA Streaming – WinCC OA debouncing example
1st change: timestamp T1 @0ms
{ID,T1,V0,UNIT}
Example: value DPE updated 20ms after timestamp DPE
Initial DPEs values: {ID, T0, V0, UNIT}
2nd change: value V1 @20ms
{ID,T1,V1,UNIT}
{ID,T1,V0,UNIT}
DEBOUNCING TIME PERIOD 30ms
{ID,T1,V1,UNIT}
 Period end
Period start 

## Slide 9: Next steps
Imminent deployment in PROD (Update 09.04.2019 : 100% completed ;-)
  All RealTime measurements
    Already test-streaming ~40% as we speak 
WinCC OA data exploitation via web & mobile applications
Discuss with (known) REMUS external DIP subscribers about Kafka adoption
  ATLAS
  CMS
  TI (C2MON)
WinCC OA data ingestion via Kafka driver (Update 09.04.2019 : completed)
  Measurements, events, etc. from new devices (i.e. IOT)
Link DPEs, in real time, with ACLs, between several WinCC OA systems!

## Slide 10: KAFKA – WinCC OA Data Ingestion (slide added on 09.04.2019)
The KAFKA WinCC OA driver can subscribe to topics and ingest data:
  Generically addressed with the WinCC OA Kafka driver
  KAFKA TOPIC$KAFKA KEY
    Ex: remustest_demo$CROME_1273.Meas.AvgValue
Example practical application: link two WinCCOA SCADA Systems
Stream from `remus_test` system
to `remustest_demo` topic
Ingest into `System1` from
`remustest_demo` topic
Try out this demo WinCC KAFKA consumer application:
  kafka-consumer-demo on gitlab
e-group ACLs

## Slide 11: Key takeaways
Use of Kafka for REMUS RealTime streaming
  Tie off DIP dependencies
  Open the door for new solutions
Generic WinCC OA Kafka driver
  Stream and ingest any WinCC OA DPs to the IT infrastructure
  Debouncing mechanism for streaming to cope with WinCC OA design if needed
  Small code base: https://gitlab.cern.ch/hse-see-co/WCCDrivers/kafka
Kafka clusters available from GPN and TN
  Thank you IT-DB !
Open for collaborative development and promotion of KAFKA CERN-wise

## Slide 12: Q&A

## Slide 14: REMUS Architecture

## Slide 15: REMUS – Main Functionalities
Control
Data Acquisition
Supervision
3 200
Channels
500
Stations
1 000
Meas./sec
600K
Data Points
24
Station Types
Data Archiving
38Bn Meas./year 2Bn after reduction
Data Visualization
GUI Editor
Application Editor
Online
Control/Command
46k parameters
Client
Supervision
Client
626 Synoptic
Alarm Screen
Client
82K Alarms defined
8Bn Meas.
Data Exchange
LASER DIP Meas. DB
18 Applications
REMUS Functional Diagram